## Data Retention Checker
Data Retention Settings Configuration Checker
Input Parameters:
1. Questions About Your SNMP Devices
Total Number Of Managed Metered PDUs - Range 1-5,000 | 1000
Average Number Of Managed Metered PDU Outlets - Range 1-30 | 20 | table name | max size (rows)
2. Questions About Your Power IQ Settings |  | outlet_readings | 2400000
2.1 Power IQ Polling Settings |  | pdu_readings | 2400
Sample Interval (minutes) | 1 | outlet_readings_rollup - hour | 960000
2.2 Power IQ Data Retention Settings |  | outlet_readings_rollup - day | 7800000
Retain Raw Data (hours) - Default is 2 | 2 | outlet_readings_rollup - month | 1200000
Retain Hourly Data (days) - Default is 2 | 2 | pdu_readings_rollup - hour | 960
Retain Daily Averages of Data (months) - Default is 13 | 13 | pdu_readings_rollup - day | 7800
Retain Monthly Averages of Data (years) - Default is 5 | 5 | pdu_readings_rollup - month | 1200
3. Questions About Your Data Storage Capacity |  | Estimated database size in rows: | 12372360
Virtual Appliance Datastore or Raritan Appliance Hard Disk - Range 80-160GB | 160 | Estimated database size in GB: | 6.9712
Output Information:
Configuration Pass/Fail | PASS
Steady State Database Utilization | 14.23%
If Configuration Fails Consider The Following Changes:
Reduce Raw Data Retenton
Reduce Hourly Data Retenton
Increase The Sample Interval
Size on disk in bytes | 605
Assigned to database partition, in GB | 49

## Sensor Reading CSV Checker
Sensor Reading CSVs Configuration Checker
Input Parameters:
1. Questions About Your SNMP Devices
Number of managed Raritan PX2 PDUs | 10
Number of managed Raritan PX1 PDUs | 100
Number of managed non-Raritan PDUs | 0
2. Questions About Your Power IQ Settings |  | outlet_readings | #VALUE!
2.1 Power IQ Polling Settings |  | pdu_readings | #VALUE!
Poll Interval (seconds) | 900
Sample Interval (seconds) | 60 | outlet_readings_rollup - hour | #VALUE!
2.2 Enterprise Power IQ Configuration
A local Power IQ which is reporting up to an enterprise PIQ will store its extraction data on the same partition as the sensor reading CSVs. Therefore, it is necessary to disable the writing of sensor readings to CSV when in an enterprise Power IQ configuration. Is this local Power IQ configured to report to an enterprise Power IQ? (YES/NO) | NO
3. Questions About Your Data Storage Capacity |  | Estimated database size in rows: | #VALUE!
Virtual Appliance Datastore or Raritan Appliance Hard Disk - Range 80-160GB | 160 | Estimated database size in GB: | #VALUE!
Output Information:
Configuration Pass/Warning/Fail | PASS
Disk space partition size where CSVs reside (in GB) | 20
Uncompressed daily CSV file size (GB) | 5.1224
CSV partition utilization for two uncompressed, daily CSVs | 62.09%
Estimated max disk space needed for CSVs (currently 8 days) | 13.3182
Max CSV partition utilization (8 days of compressed CSVs + 1 uncompressed) | 80.72%
If Configuration Fails Consider The Following Changes: Disable writing of sensor readings to CSV Increase poll interval and/or sample interval Decrease number of managed PDUs
If Configuration Results in Warning: Power IQ attempts to keep the past 8 days of compressed daily CSV files as well as the current daily, uncompressed CSV file on disk. A configuration that results in warning means that PIQ cannot guarantee to keep that much historical information. Compressed daily CSV files should be downloaded from PIQ as soon as possible to prevent losing any historical data.
Amount of disk space partition that Healthcheck reserves for data other than CSVs (in GB) | 3.5
Max percentage of available disk space that may be consumed by two uncompressed CSV files. Doing the calculation based on two uncompressed CSV files to provide a margin of safety. There should never be two uncompressed daily CSVs on disk at the same time. | 100%
Expected compression ratio (ZIP) | 80%
Max days of compressed CSVs kept by PIQ | 8
Size on disk in bytes | 605
Assigned to database partition, in GB | 49